## Input
User Model Input Template
Project Component Type
Item Information | Value | Units
Equipment Name
CpLiquidFlowrate |  | GPM
CpFluidHead |  | FT
CpSpeed |  | RPM
Connection Stream Information | Value | Units
Stream Name | __PREMAP_STREAM__ICPTOWE-ACCE |  | __PREMAP_STREAM__ICPTOWE-REFE
Stream Direction | Input |  | Output
<ICARUS SLOT NAME>
Material and Manhour Adjustment Information | Value
<ICARUS SLOT NAME>
Pipe Bulk Item Detail Information | Value
Line Name
<ICARUS SLOT NAME>

## Custom Rules
Correlation for Pump Efficiency
(based on Generalized Curves for Efficiency vs. Pump Specific Speed and Volumetric Flow Rate)
Reference: | http://www.pump-flo.com/company/pumpcenter/primer.pdf
Ns | Pump specific speed | =RPM * sqrt(gpm)/(head, ft^0.75)
| Pump Power, HP | =GPM * FT HEAD/(3960 * efficiency)
| Driver selection | table look-up, based on HP
4 coefficients
1/Z = | SS * ln ln GPM + II | SS | 1.6757
|  | II | -5.036
W = | C* exp(D*ln(GPM)) | C | 0.8944
|  | D | 0.1468
ln(1-efficiency) = Z*ln(Ns) + W
Efficiency = | 1- exp( Z * ln (Ns) + W)
Units
INPUT |  | Flow Rate, each | GPM | 0
(from Icarus) |  | Head | FT | 225 | defaults to 225 ft head for this example
|  | Pump Speed | RPM | 3600 | defaults to 3600 rpm for this example
CALCS | 1 | Pump Specific Speed, Ns | - | 0
(steps 1-6) | 2 | ln(GPM) | - | #NUM!
| 3 | ln(ln(GPM) |  | #NUM!
| 4 | ln(Ns) | - | #NUM!
| 5 | Z | - | #NUM!
| 6 | W | - | #NUM!
RESULT | 7 | Pump Efficiency | % | #NUM!
Comment | CM: Pump Efficiency calculated based on 1-exp(Z*ln(Ns)+W)
credit: Bob Steinberger

## Output
User Model Output Template
Project Component Type
Item Information | Value | Units
Equipment Name
CpPumpEfficiencyPercent | #NUM!
CpLiquidFlowrate | 0 | GPM
CpFluidHead | 225 | FT
CpSpeed | 3600 | RPM
CpRemarks2 | CM: Pump Efficiency calculated based on 1-exp(Z*ln(Ns)+W)
Connection Stream Information | Value | Units
Stream Name | __PREMAP_STREAM__ICPTOWE-ACCE
Stream Direction | Input
<ICARUS SLOT NAME>
Material and Manhour Adjustment Information | Value
<ICARUS SLOT NAME>
Pipe Bulk Item Detail Information | Value
Line Name
<ICARUS SLOT NAME>